|  | ##### SCHEDULE B - QUOTATION |
| --- | --- |

RFQ Title:	West Village Energy Centre – Hot Water Boilers

RFQ No:	1220-040-2016-043

CONTRACTOR

Legal Name:

Address:

Phone:

Fax:

Email:

CITY OF SURREY

City Representative:	Richard D. Oppelt, Purchasing Manager

Address:		Surrey City Hall

Finance & Technology Department – Purchasing Section

Reception Counter – 5th Floor West

13450 - 104 Avenue, Surrey, B.C., Canada, V3T 1V8

E-mail for PDF Files:	purchasing@surrey.ca

1.	If this Quotation is accepted by the City, a contract will be created as described in:

(a)	the Agreement;

(b)	the RFQ; and

(c)	other terms, if any, that are agreed to by the parties in writing.

2.	Capitalized terms used and not defined in this Quotation will have the meanings given to them in the Agreement and RFQ.  Except as specifically modified by this Quotation, all terms, conditions, representations, warranties and covenants as set out in the Agreement and RFQ will remain in full force and effect.

3.	I/We have reviewed the RFQ Attachment 1 – Draft Agreement. If requested by the City, I/we would be prepared to enter into that Agreement, amended by the following departures (list, if any):

Section			Requested Departure(s) / Alternative(s)

4.	The City requires that the successful Contractor have the following in place before providing the Goods and Services:

a)	Workers’ Compensation Board coverage in good standing and further, if an “Owner Operator” is involved, personal operator protection (P.O.P.) will be provided,

Workers' Compensation Registration Number ___________________________;

(b)	Prime Contractor qualified coordinator is Name:  _______________

and Contact Number:  _________________________;

(c)	Insurance coverage for the amounts required in the proposed Agreement as a minimum, naming the City as additional insured and generally in compliance with the City’s sample insurance certificate form available on the City’s Website Standard Certificate of Insurance;

(d)	City of Surrey or Intermunicipal Business License:  Number ________________;

(e)	If the Contractor’s Goods and Services are subject to GST, the Contractor’s GST Number is _____________________________________; and

(f)	If the Contractor is a company, the company name indicated above is registered with the Registrar of Companies in the Province of British Columbia, Canada, Incorporation Number ___________________________________.

As of the date of this Quotation, we advise that we have the ability to meet all of the above requirements except as follows (list, if any):

Requested Departure(s) / Alternative(s)

5.	The Contractor acknowledges that the departures it has requested in Sections 3 and 4 of this Quotation will not form part of the Agreement unless and until the City agrees to them in writing by initialing or otherwise specifically consenting in writing to be bound by any of them.

SECTION B-1

Changes and Additions to Specifications:

6.	In addition to the warranties provided in the Agreement, this Quotation includes the following warranties:

7.	I/We have reviewed the RFQ Attachment 1, Schedule A – Specifications of Goods and Scope of Services, to Attachment 1.  If requested by the City, I/we would be prepared to meet those requirements, amended by the following departures and additions (list, if any):

Requested Departure(s) / Alternative(s) / Addition(s)

SECTION B-2

Fees and Payments

8.	The Contractor offers to supply to the City of Surrey the Goods and Services for the prices plus applicable taxes as follows:

Base Bid:

| Item | Description | Qty | Total Price |
| --- | --- | --- | --- |
| A | 1000 BHP Hot Water Boiler Package | 1 |  |
| B | 1000 BHP Hot Water Boiler Package | 1 |  |
| C | 300 BHP Hot Water Boiler Package | 1 |  |
| D | Master Boiler Communication Gateway/Controller | 1 |  |
| E | Engineering Submittals | 1 Lot |  |
| F | Site Services, Training, and Final Documentation | 1 Lot |  |
| G | Delivery FOB Site | 1 Lot |  |
|  | Subtotal: |  |  |
|  | GST 5%: |  |  |
|  | Total Quotation Price: |  |  |

Optional pricing:

The following is a list of Optional Prices to the Work and forms part of this RFQ, upon the acceptance of any of the Optional Prices.  Do not include GST and do not state a revised Total Quotation Price.

| Item | Description | Qty | Total Price |
| --- | --- | --- | --- |
| A.1 | 1500 BHP Hot Water Boiler Package (option in place of one 1000 BHP boiler) | 1 |  |
| A.2 | Site Services, Training, and Final Documentation | 1 Lot |  |
| A.3 | Delivery FOB Site | 1 Lot |  |
|  | A. Total |  |  |
| B.1 | 300 BHP Hot Water Boiler Package (option to add a fourth boiler) | 1 |  |
| B.2 | Site Services, Training, and Final Documentation | 1 Lot |  |
| B.3 | Delivery FOB Site | 1 Lot |  |
|  | B. Total |  |  |
| C.1 | 100 BHP Condensing Hot Water Boiler Package (option to add a fourth boiler) | 1 |  |
| C.2 | Site Services, Training, and Final Documentation | 1 Lot |  |
| C.3 | Delivery FOB Site | 1 Lot |  |
|  | C. Total |  |  |
| D.1 | 300 BHP Condensing Hot Water Boiler Package (option to add a fourth boiler) | 1 |  |
| D.2 | Site Services, Training, and Final Documentation | 1 Lot |  |
| D.3 | Delivery FOB Site | 1 Lot |  |
|  | D. Total |  |  |
| E.1 | Economizer for 300 BHP Hot Water Boiler Package | 1 |  |
| E.2 | Site Services, Training, and Final Documentation | 1 Lot |  |
| E.3 | Delivery FOB Site | 1 Lot |  |
|  | E. Total |  |  |

Separate pricing:

The following is a list of Separate Prices to the Work and forms part of this RFQ, upon the acceptance of any of the Separate Prices.  The Separate Prices are an addition or a deduction to the Total Quotation Price and do not include GST.  DO NOT state a revised Total Quotation Price.

One (1) year scheduled maintenance contract.  $________________

Two (2) year scheduled maintenance contract.  $________________

Five (5) year scheduled maintenance contract.  $________________

Recommended Spare Parts – Priced List

Delivery and Submittals:

Documentation Submittals will be provided _____________ weeks after notice to proceed.

Delivery of Equipment, FOB Site, will occur ________ weeks after receipt of submittal drawings with comments.

Delivery delays due to rejected or unacceptable submittals will not be cause for the extension of the delivery period indicated above.

Variations from Base Bid

We submit herein a list of alternates (that will increase or reduce the base cost) including price revisions to our Quotation Price for the alternatives and variations we propose to the Specifications.  The deductions may be applied singly or collectively to the Quotation Proce.  We understand that should an alternative or variation be accepted by the City, it will be included in the contract documents as an addendum to the drawings and specifications, and not issued as a change order.

None of the following variation sums have been included in the base Quotation Price. (Attach additional page(s) as required).

Substitution/Alternates/Variations	Add/Deduct

___________________________________                $__________________________

___________________________________                $__________________________

___________________________________                $__________________________

___________________________________                $__________________________

___________________________________                $__________________________

Surrey West Village Energy Centre – Hot Water Boiler Performance Datasheet

Boiler Model:___________________; Output: 1000 BHP thermal

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.981 | 2.45 | 4.91 | 7.36 | 9.81 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 120 | 120 | 120 | 120 | 120 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 75 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Boiler Model:___________________; Output: 1000 BHP thermal

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.981 | 2.45 | 4.91 | 7.36 | 9.81 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 120 | 120 | 120 | 120 | 120 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 60 |
| LEAVING WATER TEMPERATURE | °C | 80 | 80 | 80 | 80 | 80 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

Boiler Model:___________________; Output: 300 BHP thermal

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.29 | 0.74 | 1.47 | 2.21 | 2.943 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 36 | 36 | 36 | 36 | 36 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 75 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Boiler Model:___________________; Output: 300 BHP thermal

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.29 | 0.74 | 1.47 | 2.21 | 2.943 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 36 | 36 | 36 | 36 | 36 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 60 |
| LEAVING WATER TEMPERATURE | °C | 80 | 80 | 80 | 80 | 80 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

Boiler Model:___________________; Output: 300 BHP thermal - Optional

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.29 | 0.74 | 1.47 | 2.21 | 2.943 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 36 | 36 | 36 | 36 | 36 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 75 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Boiler Model:___________________; Output: 1500 BHP thermal - Optional

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 1.47 | 3.68 | 7.36 | 11.04 | 14.72 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 180 | 180 | 180 | 180 | 180 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 75 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Boiler Model:___________________; Output: 1500 BHP thermal - Optional

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 1.47 | 3.68 | 7.36 | 11.04 | 14.72 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 180 | 180 | 180 | 180 | 180 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 60 |
| LEAVING WATER TEMPERATURE | °C | 80 | 80 | 80 | 80 | 80 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

Boiler Model:___________________; Output: 300 BHP thermal - Optional

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.29 | 0.74 | 1.47 | 2.21 | 2.943 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S | 36 | 36 | 36 | 36 | 36 |
| ENTERING WATER TEMPERATURE | °C |  |  |  |  | 60 |
| LEAVING WATER TEMPERATURE | °C | 80 | 80 | 80 | 80 | 80 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

Condensing Boiler Model:___________________; Output: 300 BHP thermal - Optional

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.294 | 0.736 | 1.47 | 2.21 | 2.94 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S |  |  |  |  |  |
| ENTERING WATER TEMPERATURE | °C | 50 | 50 | 50 | 50 | 50 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Condensing Boiler Model:___________________; Output: 300 BHP thermal - Optional

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.294 | 0.736 | 1.47 | 2.21 | 2.94 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S |  |  |  |  |  |
| ENTERING WATER TEMPERATURE | °C | 40 | 40 | 40 | 40 | 40 |
| LEAVING WATER TEMPERATURE | °C | 70 | 70 | 70 | 70 | 70 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

Condensing Boiler Model:___________________; Output: 100 BHP thermal - Optional

SEASON: WINTER

Fuel:  Natural gas;  38.2 MJ/M3 (HHV)

Ambient Air for Combustion: 10 C at 40% Relative Humidity

Site Elevation: 110 meters Above Sea Level

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.098 | 0.245 | 0.491 | 0.736 | 0.981 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S |  |  |  |  |  |
| ENTERING WATER TEMPERATURE | °C | 50 | 50 | 50 | 50 | 50 |
| LEAVING WATER TEMPERATURE | °C | 95 | 95 | 95 | 95 | 95 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

| ASME Boiler Heating Surface area (total), M2 |  |
| --- | --- |
| Furnace Volume; M3 |  |
| Minimum Flowrate (L/s) |  |

Vendor______________________________

Condensing Boiler Model:___________________; Output: 100 BHP thermal - Optional

SEASON: SUMMER

Fuel:  Natural gas;  38.8 MJ/M3 (HHV)

Ambient Air for Combustion: 20 C at 40% Relative Humidity

Site Elevation: 110 meters ASL

| FIRING RATE | % | 10 | 25 | 50 | 75 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| BOILER OUTPUT MWt |  | 0.098 | 0.245 | 0.491 | 0.736 | 0.981 |
| OUTLET OPERATING PRESSURE | kPag | 275 | 275 | 275 | 275 | 275 |
| FLOWRATE | L/S |  |  |  |  |  |
| ENTERING WATER TEMPERATURE | °C | 40 | 40 | 40 | 40 | 40 |
| LEAVING WATER TEMPERATURE | °C | 70 | 70 | 70 | 70 | 70 |
| WATER SIDE PRESSURE DROP | kPa |  |  |  |  |  |
| FLUE GAS TEMP. LVG. BOILER | °C |  |  |  |  |  |
| STACK TEMPERATURE | °C |  |  |  |  |  |
| NOx @ 3% O2 dry | ppm |  |  |  |  |  |
| CO | ppm |  |  |  |  |  |
| FUEL RATE | Kg/Hr |  |  |  |  |  |
| EXCESS AIR | % |  |  |  |  |  |
| COMBUSTION AIR RATE | Kg/Hr |  |  |  |  |  |
| COMBUSTION AIR TEMPERATURE | °C |  |  |  |  |  |
| FLUE GAS RATE | Kg/Hr |  |  |  |  |  |
| RELEASE RATE | kW / M2 |  |  |  |  |  |
| LIBERATION RATE | kW / M3 |  |  |  |  |  |
| LOSSES |  |  |  |  |  |  |
| Dry gas loss | % |  |  |  |  |  |
| H2O+H2 in fuel | % |  |  |  |  |  |
| H2O in air | % |  |  |  |  |  |
| Radiation | % |  |  |  |  |  |
| Manufacturer's margin | % |  |  |  |  |  |
| Unaccounted for losses | % |  |  |  |  |  |
| TOTAL LOSSES | % |  |  |  |  |  |
| BOILER EFFICIENCY; Fuel to Water (HHV) | % |  |  |  |  |  |

Vendor______________________________

SECTION B-3

Time Schedule:

9.	Contractors should provide an estimated schedule, with major item descriptions and times indicating a commitment to provide the Goods and perform the Services within the time specified (use the spaces provided and/or attach additional pages, if necessary).

MILESTONE DATES __________________________________

| ##### ACTIVITY | ##### SCHEDULE |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |

SECTION B-4

Key Personnel & Sub-Contractors:

10.	Contractor should provide information on the background and experience of all key personnel proposed to provide the Goods and Services (use the spaces provided and/or attach additional pages, if necessary):

Key Personnel

| Name: |  |
| --- | --- |
| Experience: |  |
| Dates: |  |
| Project Name: |  |
| Responsibility: |  |

11.	Contractor should provide the following information on the background and experience of all sub-contractors and material suppliers proposed to undertake a portion of the Goods and Services (use the spaces provided and/or attach additional pages, if necessary):

| Description Of Goods & Services | Sub-Contractors & Material Suppliers Names | Years Of Working With Contractor | Telephone Number And Email |
| --- | --- | --- | --- |

SECTION B-5

Experience and References:

12.	Contractor's relevant experience and qualifications in delivering Goods and Services similar to those required by the Agreement (use the spaces provided and/or attach additional pages, if necessary):

13.	Contractor's relevant references (name and telephone number) (use the spaces provided and/or attach additional pages, if necessary).  The City's preference is to have a minimum of three references.  Previous clients of the Contractor may be contacted at the City’s discretion.

14.	Contractor to describe their sustainability initiatives relating to the environmental impacts. The environmental attributes (green) of their Goods and Services. Anticipated objectives (e.g. carbon neutral by 2015). Information pertaining to their environmental policies, programs and practices. Confirm that the Contractor complies with any applicable objective.

Metro Vancouver’s Non-Road Diesel Engine Emissions Regulation By-law:

15.	Contractor should confirm they are in compliance with By-law (if applicable):

 Applicable as follows    Not applicable to this project

| No. | Equipment Description | Engine Tier Designation | Engine Registration Number as Issued by Metro Vancouver |
| --- | --- | --- | --- |
| 1 |  |  Tier 0 or  Tier 1 |  |
| 2 |  |  Tier 0 or  Tier 1 |  |
| 3 |  |  Tier 0 or  Tier 1 |  |
| 4 |  |  Tier 0 or  Tier 1 |  |
| 5 |  |  Tier 0 or  Tier 1 |  |

16.	I/We the undersigned duly authorized representatives of the Contractor, having received and carefully reviewed the RFQ and the Agreement, submit this Quotation in response to the RFQ.

This Quotation is offered by the Contractor this _______ day of _______________, 201_.

CONTRACTOR

I/We have the authority to bind the Contractor

| ________________________________________ (Legal Name of Contractor) _________________________________________ (Signature of Authorized Signatory) _______________________________________ (Print Name and Position of Authorized Signatory) | ________________________________________ (Signature of Authorized Signatory) ________________________________________ (Print Name and Position of Authorized Signatory) |
| --- | --- |

This Quotation is accepted by the City this _______ day of _______________, 201_.

CITY OF SURREY

| ________________________________________ (Signature of Authorized Signatory) _________________________________________ (Print Name and Position of Authorized Signatory) | ________________________________________ (Signature of Purchasing Representative ________________________________________ (Print Name of Purchasing Representative) |
| --- | --- |